{"text_format":"2","workbook":"xls","n_sheets":4,"sheets":["Règles d'@IP","@Modbus","@Profibus PRM","@STB de MDCBox"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Règles d'@IP","index":0,"n_rows":59,"n_cols":8,"rows_kept":59,"cut":false,"hidden":false,"merged":[[23,0,23,1],[24,0,24,1],[0,0,0,3],[15,0,15,3],[17,4,18,4],[20,0,20,7],[21,0,21,1],[22,0,22,1]],"flags":["formulas_cached_only"]}
["Règle d'adressage des sous-réseau par <site>"]
["Type d'Equipement","@IP min","@IP max","Nombre d'équipements adressables"]
["Serveur ClearSCADA","10.<site>.0.1",null,1]
["Imprimante, PC client ViewX, 2ème serveur…","10.<site>.0.2","10.<site>.0.254",253]
["PVBOX","10.<site>.1.xxx","10.<site>.100.xxx",100]
["GRIDBOX","10.<site>.101.xxx","10.<site>.110.xxx",10]
["CPU","10.<site>.<PVBOX/GRIDBOX>.1",null,1]
["NOR","10.<site>.<PVBOX/GRIDBOX>.2",null,1]
["NOE","10.<site>.<PVBOX/GRIDBOX>.3",null,1]
["PRM","10.<site>.<PVBOX>.11","10.<site>.<PVBOX>.20",10]
["TSXETG100","10.<site>.<PVBOX/GRIDBOX>.21","10.<site>.<PVBOX/GRIDBOX>.40",20]
["Switch Ethernet","10.<site>.<PVBOX/GRIDBOX>.41","10.<site>.<PVBOX/GRIDBOX>.50",10]
["DCBox monitorée","10.<site>.<PVBOX>.51","10.<site>.<PVBOX>.60",10]
["Energy meter TCP/IP (ex. ION8600)","10.<site>.<PVBOX/GRIDBOX>.61","10.<site>.<PVBOX/GRIDBOX>.70",10]
[]
["Règle d'adressage des identifiants DNP3 par <site>"]
["Type d'Equipement","Identifiant min","Identifiant max","Nombre d'équipements adressables","remarques"]
["GRIDBOX","<site> * 10 + 101","<site> * 10 + 110",10,"Cette règle permet de garder une homogénéité avec les règles d'adressages IP lorsque plusieurs sites sont créé sur un même serveur ClearSCADA, car le DNP3 Identifier d'une NOR doit être unique pour tout le projet. Rappel : le DNP3 Id d'une outstation NOR peut aller de 1 à 65520 (0 à 65519 dans ClearSCADA)"]
["PVBOX","<site> * 10 + 1","<site> * 10 + 100",100]
[]
["Exemple d'adressage"]
["EQUIPEMENT",null,null,"PVBOX 1","PVBOX 2","GRIDBOX","Subnet Mask","remarques"]
["Data Center / NTP Server",null,"xxx.xxx.xxx.xxx",null,null,null,"xxx.xxx.xxx.xxx"]
["Supervision CS",null,"10.001.000.001",null,null,null,"255.255.000.000"]
["Routeur ETIC vers Data Center",null,"10.001.000.002",null,null,null,"255.255.000.000"]
["GridBox","M340 CPU2020",null,null,null,"10.001.101.001","255.255.000.000","La Grid Box doit pouvoir accéder aux CPU des PVBox et au routeur ETIC"]
["GridBox","M340 NOR0200",null,null,null,"10.001.101.002","255.255.000.000","DNP3 (Identifiant = 101)"]
["GridBox","M340 NOE0110",null,null,null,"10.001.101.003","255.255.000.000","NTP"]
["GridBox","Passerelle Ethernet / Modbus (PROT) TSXETG100 1",null,null,null,"10.001.101.021","255.255.000.000"]
["GridBox","Passerelle Ethernet / Modbus (PROT) TSXETG100 2",null,null,null,"10.001.101.022","255.255.000.000"]
["GridBox","Passerelle Ethernet / Modbus (PROT) TSXETG100 3",null,null,null,"10.001.101.023","255.255.000.000"]
["GridBox","Passerelle Ethernet / Modbus (PROT) TSXETG100 4",null,null,null,"10.001.101.024","255.255.000.000"]
["GridBox","Switch Ethernet",null,null,null,"10.001.101.041","255.255.000.000"]
["GridBox","EM Del ION8600",null,null,null,"10.001.101.061","255.255.000.000"]
["PVBox","M340 CPU2020",null,"10.001.001.001","10.001.002.001",null,"255.255.000.000","La Grid Box doit pouvoir accéder aux CPU des PVBox"]
["PVBox","M340 NOR0200",null,"10.001.001.002","10.001.002.002",null,"255.255.000.000","DNP3 (Identifiant = 1)"]
["PVBox","M340 NOE0110",null,"10.001.001.003","10.001.002.003",null,"255.255.000.000","NTP"]
["PVBox","Profibus Remote Master 1",null,"10.001.001.011","10.001.002.011",null,"255.255.000.000"]
["PVBox","Profibus Remote Master 2",null,"10.001.001.012","10.001.002.012",null,"255.255.000.000"]
["PVBox","Profibus Remote Master 3",null,"10.001.001.013","10.001.002.013",null,"255.255.000.000"]
["PVBox","Profibus Remote Master 4",null,"10.001.001.014","10.001.002.014",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV1) TSXETG100 1",null,"10.001.001.021","10.001.002.021",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV2) TSXETG100 2",null,"10.001.001.022","10.001.002.022",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV3) TSXETG100 3",null,"10.001.001.023","10.001.002.023",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV4) TSXETG100 4",null,"10.001.001.024","10.001.002.024",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV5) TSXETG100 5",null,"10.001.001.025","10.001.002.025",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV6) TSXETG100 6",null,"10.001.001.026","10.001.002.026",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV7) TSXETG100 7",null,"10.001.001.027","10.001.002.027",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( INV8) TSXETG100 8",null,"10.001.001.028","10.001.002.028",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( EM, AUX, PROT) TSXETG100 9",null,"10.001.001.031","10.001.002.031",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( EM, AUX, PROT) TSXETG100 10",null,"10.001.001.032","10.001.002.032",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( EM, AUX, PROT) TSXETG100 11",null,"10.001.001.033","10.001.002.033",null,"255.255.000.000"]
["PVBox","Passerelle Ethernet / Modbus ( EM, AUX, PROT) TSXETG100 12",null,"10.001.001.034","10.001.002.034",null,"255.255.000.000"]
["PVBox","Switch Ethernet 1",null,"10.001.001.041","10.001.002.041",null,"255.255.000.000"]
["PVBox","Monitored DCBOX 1",null,"10.001.001.051","10.001.002.051",null,"255.255.000.000"]
["PVBox","Monitored DCBOX 2",null,"10.001.001.052","10.001.002.052",null,"255.255.000.000"]
["PVBox","Monitored DCBOX 3",null,"10.001.001.053","10.001.002.053",null,"255.255.000.000"]
["PVBox","Monitored DCBOX 4",null,"10.001.001.054","10.001.002.054",null,"255.255.000.000"]
["PVBox","EM Del ION8600",null,"10.001.001.061","10.001.002.061",null,"255.255.000.000"]

{"sheet":"@Modbus","index":1,"n_rows":11,"n_cols":6,"rows_kept":11,"cut":false,"hidden":false,"merged":[[0,0,0,1],[1,0,4,0],[1,1,4,1],[6,0,10,0],[7,1,10,1]],"flags":["formulas_cached_only"]}
["PASSERELLE",null,"EQT","@Modbus Slave","EQT","@Modbus Slave"]
["GridBox","Passerelle Ethernet / Modbus ( EM, AUX, PROT) TSXETG100\nGateway number and equipement repartition, depends on appplication","EM_AUX","20..29","S48","40..49"]
[null,null,"EM_DEL","30..39","S40","50..59"]
[null,null,"S48","40..49","S41","60..69"]
[null,null,"S40","50..59","T20","70..79"]
[]
["PVBox","Gateway Ethernet / Modbus TSXETG100\nOne per Inverter","GT500",200,"XC500",248]
[null,"Passerelle Ethernet / Modbus ( EM, AUX, PROT) TSXETG100\nGateway number and equipement repartition, depends on appplication","EM_PROD","1..9"]
[null,null,"S10","10..19"]
[null,null,"EM_AUX","20..29"]
[null,null,"EM_DEL","30..39"]

{"sheet":"@Profibus PRM","index":2,"n_rows":59,"n_cols":13,"rows_kept":59,"cut":false,"hidden":false,"merged":[[42,1,42,3],[42,4,42,6],[42,7,42,9],[42,10,42,12],[49,1,49,3],[49,4,49,6],[49,7,49,9],[49,10,49,12],[28,1,28,3],[28,4,28,6],[28,7,28,9],[28,10,28,12],[35,1,35,3],[35,4,35,6],[35,7,35,9],[35,10,35,12],[14,1,14,3],[14,4,14,6],[14,7,14,9],[14,10,14,12],[21,1,21,3],[21,4,21,6],[21,7,21,9],[21,10,21,12],[0,1,0,3],[0,4,0,6],[0,7,0,9],[0,10,0,12],[7,1,7,3],[7,4,7,6],[7,7,7,9],[7,10,7,12]],"flags":["formulas_cached_only"]}
["PVBOX",1,null,null,2,null,null,3,null,null,4]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",0,"TCSEGPA23F14F000","10.1.1.11",4,"TCSEGPA23F14F004","10.1.2.11",8,"TCSEGPA23F14F008","10.1.3.11",12,"TCSEGPA23F14F012","10.1.4.11"]
["PRM 2",1,"TCSEGPA23F14F001","10.1.1.12",5,"TCSEGPA23F14F005","10.1.2.12",9,"TCSEGPA23F14F009","10.1.3.12",13,"TCSEGPA23F14F013","10.1.4.12"]
["PRM 3",2,"TCSEGPA23F14F002","10.1.1.13",6,"TCSEGPA23F14F006","10.1.2.13",10,"TCSEGPA23F14F010","10.1.3.13",14,"TCSEGPA23F14F014","10.1.4.13"]
["PRM 4",3,"TCSEGPA23F14F003","10.1.1.14",7,"TCSEGPA23F14F007","10.1.2.14",11,"TCSEGPA23F14F011","10.1.3.14",15,"TCSEGPA23F14F015","10.1.4.14"]
[]
["PVBOX",5,null,null,6,null,null,7,null,null,8]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",16,"TCSEGPA23F14F016","10.1.5.11",20,"TCSEGPA23F14F020","10.1.6.11",24,"TCSEGPA23F14F024","10.1.7.11",28,"TCSEGPA23F14F028","10.1.8.11"]
["PRM 2",17,"TCSEGPA23F14F017","10.1.5.12",21,"TCSEGPA23F14F021","10.1.6.12",25,"TCSEGPA23F14F025","10.1.7.12",29,"TCSEGPA23F14F029","10.1.8.12"]
["PRM 3",18,"TCSEGPA23F14F018","10.1.5.13",22,"TCSEGPA23F14F022","10.1.6.13",26,"TCSEGPA23F14F026","10.1.7.13",30,"TCSEGPA23F14F030","10.1.8.13"]
["PRM 4",19,"TCSEGPA23F14F019","10.1.5.14",23,"TCSEGPA23F14F023","10.1.6.14",27,"TCSEGPA23F14F027","10.1.7.14",31,"TCSEGPA23F14F031","10.1.8.14"]
[]
["PVBOX",9,null,null,10,null,null,11,null,null,12]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",32,"TCSEGPA23F14F032","10.1.9.11",36,"TCSEGPA23F14F036","10.1.10.11",40,"TCSEGPA23F14F040","10.1.11.11",44,"TCSEGPA23F14F044","10.1.12.11"]
["PRM 2",33,"TCSEGPA23F14F033","10.1.9.12",37,"TCSEGPA23F14F037","10.1.10.12",41,"TCSEGPA23F14F041","10.1.11.12",45,"TCSEGPA23F14F045","10.1.12.12"]
["PRM 3",34,"TCSEGPA23F14F034","10.1.9.13",38,"TCSEGPA23F14F038","10.1.10.13",42,"TCSEGPA23F14F042","10.1.11.13",46,"TCSEGPA23F14F046","10.1.12.13"]
["PRM 4",35,"TCSEGPA23F14F035","10.1.9.14",39,"TCSEGPA23F14F039","10.1.10.14",43,"TCSEGPA23F14F043","10.1.11.14",47,"TCSEGPA23F14F047","10.1.12.14"]
[]
["PVBOX",13,null,null,14,null,null,15,null,null,16]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",48,"TCSEGPA23F14F048","10.1.13.11",52,"TCSEGPA23F14F052","10.1.14.11",56,"TCSEGPA23F14F056","10.1.15.11",60,"TCSEGPA23F14F060","10.1.16.11"]
["PRM 2",49,"TCSEGPA23F14F049","10.1.13.12",53,"TCSEGPA23F14F053","10.1.14.12",57,"TCSEGPA23F14F057","10.1.15.12",61,"TCSEGPA23F14F061","10.1.16.12"]
["PRM 3",50,"TCSEGPA23F14F050","10.1.13.13",54,"TCSEGPA23F14F054","10.1.14.13",58,"TCSEGPA23F14F058","10.1.15.13",62,"TCSEGPA23F14F062","10.1.16.13"]
["PRM 4",51,"TCSEGPA23F14F051","10.1.13.14",55,"TCSEGPA23F14F055","10.1.14.14",59,"TCSEGPA23F14F059","10.1.15.14",63,"TCSEGPA23F14F063","10.1.16.14"]
[]
["PVBOX",17,null,null,18,null,null,19,null,null,20]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",64,"TCSEGPA23F14F064","10.1.17.11",68,"TCSEGPA23F14F068","10.1.18.11",72,"TCSEGPA23F14F072","10.1.19.11",76,"TCSEGPA23F14F076","10.1.20.11"]
["PRM 2",65,"TCSEGPA23F14F065","10.1.17.12",69,"TCSEGPA23F14F069","10.1.18.12",73,"TCSEGPA23F14F073","10.1.19.12",77,"TCSEGPA23F14F077","10.1.20.12"]
["PRM 3",66,"TCSEGPA23F14F066","10.1.17.13",70,"TCSEGPA23F14F070","10.1.18.13",74,"TCSEGPA23F14F074","10.1.19.13",78,"TCSEGPA23F14F078","10.1.20.13"]
["PRM 4",67,"TCSEGPA23F14F067","10.1.17.14",71,"TCSEGPA23F14F071","10.1.18.14",75,"TCSEGPA23F14F075","10.1.19.14",79,"TCSEGPA23F14F079","10.1.20.14"]
[]
["PVBOX",21,null,null,22,null,null,23,null,null,24]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",80,"TCSEGPA23F14F080","10.1.21.11",84,"TCSEGPA23F14F084","10.1.22.11",88,"TCSEGPA23F14F088","10.1.23.11",92,"TCSEGPA23F14F092","10.1.24.11"]
["PRM 2",81,"TCSEGPA23F14F081","10.1.21.12",85,"TCSEGPA23F14F085","10.1.22.12",89,"TCSEGPA23F14F089","10.1.23.12",93,"TCSEGPA23F14F093","10.1.24.12"]
["PRM 3",82,"TCSEGPA23F14F082","10.1.21.13",86,"TCSEGPA23F14F086","10.1.22.13",90,"TCSEGPA23F14F090","10.1.23.13",94,"TCSEGPA23F14F094","10.1.24.13"]
["PRM 4",83,"TCSEGPA23F14F083","10.1.21.14",87,"TCSEGPA23F14F087","10.1.22.14",91,"TCSEGPA23F14F091","10.1.23.14",95,"TCSEGPA23F14F095","10.1.24.14"]
[]
["PVBOX",25,null,null,26,null,null,27,null,null,28]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",96,"TCSEGPA23F14F096","10.1.25.11",100,"TCSEGPA23F14F100","10.1.26.11",104,"TCSEGPA23F14F104","10.1.27.11",108,"TCSEGPA23F14F108","10.1.28.11"]
["PRM 2",97,"TCSEGPA23F14F097","10.1.25.12",101,"TCSEGPA23F14F101","10.1.26.12",105,"TCSEGPA23F14F105","10.1.27.12",109,"TCSEGPA23F14F109","10.1.28.12"]
["PRM 3",98,"TCSEGPA23F14F098","10.1.25.13",102,"TCSEGPA23F14F102","10.1.26.13",106,"TCSEGPA23F14F106","10.1.27.13",110,"TCSEGPA23F14F110","10.1.28.13"]
["PRM 4",99,"TCSEGPA23F14F099","10.1.25.14",103,"TCSEGPA23F14F103","10.1.26.14",107,"TCSEGPA23F14F107","10.1.27.14",111,"TCSEGPA23F14F111","10.1.28.14"]
[]
["PVBOX",29,null,null,30,null,null,31,null,null,32]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["PRM 1",112,"TCSEGPA23F14F112","10.1.29.11",116,"TCSEGPA23F14F116","10.1.30.11",120,"TCSEGPA23F14F120","10.1.31.11",124,"TCSEGPA23F14F124","10.1.32.11"]
["PRM 2",113,"TCSEGPA23F14F113","10.1.29.12",117,"TCSEGPA23F14F117","10.1.30.12",121,"TCSEGPA23F14F121","10.1.31.12",125,"TCSEGPA23F14F125","10.1.32.12"]
["PRM 3",114,"TCSEGPA23F14F114","10.1.29.13",118,"TCSEGPA23F14F118","10.1.30.13",122,"TCSEGPA23F14F122","10.1.31.13",126,"TCSEGPA23F14F126","10.1.32.13"]
["PRM 4",115,"TCSEGPA23F14F115","10.1.29.14",119,"TCSEGPA23F14F119","10.1.30.14",123,"TCSEGPA23F14F123","10.1.31.14",127,"TCSEGPA23F14F127","10.1.32.14"]
[]
[]
["EQT","@Profibus",null,"EQT","@Profibus"]
["PRM",0,null,"AB","1..30"]

{"sheet":"@STB de MDCBox","index":3,"n_rows":55,"n_cols":13,"rows_kept":55,"cut":false,"hidden":false,"merged":[[42,1,42,3],[42,4,42,6],[42,7,42,9],[42,10,42,12],[49,1,49,3],[49,4,49,6],[49,7,49,9],[49,10,49,12],[28,1,28,3],[28,4,28,6],[28,7,28,9],[28,10,28,12],[35,1,35,3],[35,4,35,6],[35,7,35,9],[35,10,35,12],[14,1,14,3],[14,4,14,6],[14,7,14,9],[14,10,14,12],[21,1,21,3],[21,4,21,6],[21,7,21,9],[21,10,21,12],[0,1,0,3],[0,4,0,6],[0,7,0,9],[0,10,0,12],[7,1,7,3],[7,4,7,6],[7,7,7,9],[7,10,7,12]],"flags":["formulas_cached_only"]}
["PVBOX",1,null,null,2,null,null,3,null,null,4]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",0,"STBNIP2212_000","10.1.1.51",4,"STBNIP2212_004","10.1.2.51",8,"STBNIP2212_008","10.1.3.51",12,"STBNIP2212_012","10.1.4.51"]
["MDCB 2",1,"STBNIP2212_001","10.1.1.52",5,"STBNIP2212_005","10.1.2.52",9,"STBNIP2212_009","10.1.3.52",13,"STBNIP2212_013","10.1.4.52"]
["MDCB 3",2,"STBNIP2212_002","10.1.1.53",6,"STBNIP2212_006","10.1.2.53",10,"STBNIP2212_010","10.1.3.53",14,"STBNIP2212_014","10.1.4.53"]
["MDCB 4",3,"STBNIP2212_003","10.1.1.54",7,"STBNIP2212_007","10.1.2.54",11,"STBNIP2212_011","10.1.3.54",15,"STBNIP2212_015","10.1.4.54"]
[]
["PVBOX",5,null,null,6,null,null,7,null,null,8]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",16,"STBNIP2212_016","10.1.5.51",20,"STBNIP2212_020","10.1.6.51",24,"STBNIP2212_024","10.1.7.51",28,"STBNIP2212_028","10.1.8.51"]
["MDCB 2",17,"STBNIP2212_017","10.1.5.52",21,"STBNIP2212_021","10.1.6.52",25,"STBNIP2212_025","10.1.7.52",29,"STBNIP2212_029","10.1.8.52"]
["MDCB 3",18,"STBNIP2212_018","10.1.5.53",22,"STBNIP2212_022","10.1.6.53",26,"STBNIP2212_026","10.1.7.53",30,"STBNIP2212_030","10.1.8.53"]
["MDCB 4",19,"STBNIP2212_019","10.1.5.54",23,"STBNIP2212_023","10.1.6.54",27,"STBNIP2212_027","10.1.7.54",31,"STBNIP2212_031","10.1.8.54"]
[]
["PVBOX",9,null,null,10,null,null,11,null,null,12]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",32,"STBNIP2212_032","10.1.9.51",36,"STBNIP2212_036","10.1.10.51",40,"STBNIP2212_040","10.1.11.51",44,"STBNIP2212_044","10.1.12.51"]
["MDCB 2",33,"STBNIP2212_033","10.1.9.52",37,"STBNIP2212_037","10.1.10.52",41,"STBNIP2212_041","10.1.11.52",45,"STBNIP2212_045","10.1.12.52"]
["MDCB 3",34,"STBNIP2212_034","10.1.9.53",38,"STBNIP2212_038","10.1.10.53",42,"STBNIP2212_042","10.1.11.53",46,"STBNIP2212_046","10.1.12.53"]
["MDCB 4",35,"STBNIP2212_035","10.1.9.54",39,"STBNIP2212_039","10.1.10.54",43,"STBNIP2212_043","10.1.11.54",47,"STBNIP2212_047","10.1.12.54"]
[]
["PVBOX",13,null,null,14,null,null,15,null,null,16]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",48,"STBNIP2212_048","10.1.13.51",52,"STBNIP2212_052","10.1.14.51",56,"STBNIP2212_056","10.1.15.51",60,"STBNIP2212_060","10.1.16.51"]
["MDCB 2",49,"STBNIP2212_049","10.1.13.52",53,"STBNIP2212_053","10.1.14.52",57,"STBNIP2212_057","10.1.15.52",61,"STBNIP2212_061","10.1.16.52"]
["MDCB 3",50,"STBNIP2212_050","10.1.13.53",54,"STBNIP2212_054","10.1.14.53",58,"STBNIP2212_058","10.1.15.53",62,"STBNIP2212_062","10.1.16.53"]
["MDCB 4",51,"STBNIP2212_051","10.1.13.54",55,"STBNIP2212_055","10.1.14.54",59,"STBNIP2212_059","10.1.15.54",63,"STBNIP2212_063","10.1.16.54"]
[]
["PVBOX",17,null,null,18,null,null,19,null,null,20]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",64,"STBNIP2212_064","10.1.17.51",68,"STBNIP2212_068","10.1.18.51",72,"STBNIP2212_072","10.1.19.51",76,"STBNIP2212_076","10.1.20.51"]
["MDCB 2",65,"STBNIP2212_065","10.1.17.52",69,"STBNIP2212_069","10.1.18.52",73,"STBNIP2212_073","10.1.19.52",77,"STBNIP2212_077","10.1.20.52"]
["MDCB 3",66,"STBNIP2212_066","10.1.17.53",70,"STBNIP2212_070","10.1.18.53",74,"STBNIP2212_074","10.1.19.53",78,"STBNIP2212_078","10.1.20.53"]
["MDCB 4",67,"STBNIP2212_067","10.1.17.54",71,"STBNIP2212_071","10.1.18.54",75,"STBNIP2212_075","10.1.19.54",79,"STBNIP2212_079","10.1.20.54"]
[]
["PVBOX",21,null,null,22,null,null,23,null,null,24]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",80,"STBNIP2212_080","10.1.21.51",84,"STBNIP2212_084","10.1.22.51",88,"STBNIP2212_088","10.1.23.51",92,"STBNIP2212_092","10.1.24.51"]
["MDCB 2",81,"STBNIP2212_081","10.1.21.52",85,"STBNIP2212_085","10.1.22.52",89,"STBNIP2212_089","10.1.23.52",93,"STBNIP2212_093","10.1.24.52"]
["MDCB 3",82,"STBNIP2212_082","10.1.21.53",86,"STBNIP2212_086","10.1.22.53",90,"STBNIP2212_090","10.1.23.53",94,"STBNIP2212_094","10.1.24.53"]
["MDCB 4",83,"STBNIP2212_083","10.1.21.54",87,"STBNIP2212_087","10.1.22.54",91,"STBNIP2212_091","10.1.23.54",95,"STBNIP2212_095","10.1.24.54"]
[]
["PVBOX",25,null,null,26,null,null,27,null,null,28]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",96,"STBNIP2212_096","10.1.25.51",100,"STBNIP2212_100","10.1.26.51",104,"STBNIP2212_104","10.1.27.51",108,"STBNIP2212_108","10.1.28.51"]
["MDCB 2",97,"STBNIP2212_097","10.1.25.52",101,"STBNIP2212_101","10.1.26.52",105,"STBNIP2212_105","10.1.27.52",109,"STBNIP2212_109","10.1.28.52"]
["MDCB 3",98,"STBNIP2212_098","10.1.25.53",102,"STBNIP2212_102","10.1.26.53",106,"STBNIP2212_106","10.1.27.53",110,"STBNIP2212_110","10.1.28.53"]
["MDCB 4",99,"STBNIP2212_099","10.1.25.54",103,"STBNIP2212_103","10.1.26.54",107,"STBNIP2212_107","10.1.27.54",111,"STBNIP2212_111","10.1.28.54"]
[]
["PVBOX",29,null,null,30,null,null,31,null,null,32]
[null,"Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr","Rotary SW","Role name","IP addr"]
["MDCB 1",112,"STBNIP2212_112","10.1.29.51",116,"STBNIP2212_116","10.1.30.51",120,"STBNIP2212_120","10.1.31.51",124,"STBNIP2212_124","10.1.32.51"]
["MDCB 2",113,"STBNIP2212_113","10.1.29.52",117,"STBNIP2212_117","10.1.30.52",121,"STBNIP2212_121","10.1.31.52",125,"STBNIP2212_125","10.1.32.52"]
["MDCB 3",114,"STBNIP2212_114","10.1.29.53",118,"STBNIP2212_118","10.1.30.53",122,"STBNIP2212_122","10.1.31.53",126,"STBNIP2212_126","10.1.32.53"]
["MDCB 4",115,"STBNIP2212_115","10.1.29.54",119,"STBNIP2212_119","10.1.30.54",123,"STBNIP2212_123","10.1.31.54",127,"STBNIP2212_127","10.1.32.54"]